# Annual Drinking Water Quality Report

# 2013

The Town of Sharptown, Maryland

Public Water System Identification number (PWSID) - 0220005

We're pleased to present this year's Annual Drinking Water Report. This report is designed to inform you about the quality water and services we deliver to you every day. Our constant goal is to provide you with a safe and dependable supply of drinking water. We want you to understand the efforts we make to continually improve the water treatment process and protect our water resources. We are committed to ensuring the quality of your water.

The Town of Sharptown’s source of drinking water is supplied to our customers from four underground wells. One of our wells draw water from the Nanticoke Aquifer, which is, located about 300 feet below the earth’s surface.  An aquifer is a sort of underground reservoir or deposit of water, which is tapped by drilling wells and pumping the water to the surface for distribution. The 300 feet of earth between surface sources of contamination and this underground river helps to purify the water before it actually reaches the aquifer, making it easier for us to treat before we pump it into your water distribution system.

The other two wells are at a depth of 70 feet and 90 feet below the earth’s surface, which is not a confined aquifer like the Nanticoke Aquifer, which can be susceptible to contamination from above ground sources.

Each one of our wells has a different water composition, and chemical makeup, such as different pH levels, iron and sodium, nitrates levels.  These four wells are blended together at precise levels, which deliver the best possible quality finished drinking water to our water customers.

We are sorry to report that our drinking water does not meet federal and state requirements (see page 7 for test levels). The following report is provided in compliance with federal regulations and will be provided annually. This report outlines the quality of our finished drinking water and what that quality means.

In August, 2000, the Town was awarded a grant from the Maryland Department of the Environment to establish a wellhead protection plan (source water assessment plan) for its community water system.  The plan was completed in March, 2001 by Advanced Land and Water, Inc.  The required components of this plan are: (1) mapping of an area that contributes water to the source, (2) identification of potential sources of contamination to ground water supplies and (3) determination of the susceptibility of the water supply to contamination.  Results, recommendations and map of the plan can be reviewed at the Town Hall.

If you have any questions about this report or concerning your water utility, please contact Water & Sewer Supervisor, William R. White at 410-883-3805. We want our valued customers to be informed about their water utility. If you want to learn more, please attend any of our regularly scheduled Council meetings. They are held on the first and third Mondays of every month beginning at 7:30 p.m.

The Town of Sharptown’s Water Department routinely monitors for contaminants in your drinking water according to Federal and State laws. The tables on the following pages show the results of our monitoring as required by law within the past five years. As water travels over the land or underground, it can pick up substances or contaminants such as microbes, inorganic and organic chemicals, and radioactive substances. All drinking water, including bottled drinking water, may be reasonably expected to contain at least small amounts of some contaminants.  It's important to remember that the presence of these contaminants does not necessarily pose a health risk.

Definitions

In this report you will find many terms and abbreviations you might not be familiar with. To help you better understand these terms we've provided the following definitions:

Non-Detects (ND) - laboratory analysis indicates that the constituent is not present.

Parts per million (ppm) or Milligrams per liter (mg/l) - one part per million corresponds to one minute in two years or a single penny in $10,000.

Parts per billion (ppb) or Micrograms per liter - one part per billion corresponds to one minute in 2,000 years, or a single penny in $10,000,000.

Action Level - the concentration of a contaminant which, if exceeded, triggers treatment or other requirements which a water system must follow.

Picocuries per liter (pCi/L)- picocuries per liter is a measure of the radioactivity in water.

Treatment Technique (TT) - A treatment technique is a required process intended to reduce the level of a contaminant in drinking water.

Maximum Contaminant Level - The “Maximum Allowed” (MCL) is the highest level of a contaminant that is allowed in drinking water.  MCLs are set as close to the MCLGs as feasible using the best available treatment technology.

Maximum Contaminant Level Goal - The “Goal”(MCLG) is the level of a contaminant in drinking water below which there is no known or expected risk to health.  MCLGs allow for a margin of safety.

Have Waiver – System is not susceptible to contamination from that particular chemical, not required to test.

Non-Detected Contaminants

Following is a list of potential drinking water substances that the Town of Sharptown is required to test for, but which have not been detected in the water supply in the past year. The Town is only required to provide information on those substances it has detected in the finished water supply, but is providing the complete list of required EPA sampling in order to better inform its customers about the extent of testing that is done to their water supply.

###### Contaminant         	                              Level              Year	Contaminant         		             Level          Year

Detected          Tested                                                                         Detected      Tested

1.    Total Coliform Bacteria 		 0   	2012	31.  Pentachlorophenol		<0.05	2011

2.    Fecal coliform and E.coli		 0	2012	32.  Toxaphene		 	  0	1996

3.    Combined Radium	  	 0	2003	33.  Carbon tetrachloride	 	<0.5	2013

4.    Antimony    		               <.002	2012	34.  Cadium			<0.0025	2012

5.    Asbestos (have waiver)		 0	1995	35.  o-Dichlorobenzene		<0.5	2013

6.    Glyphosate			 0	1995	36.  p-Dichlorobenzene		<0.5	2013

37.  1,2 - Dichloromethane		  0	2004

8.    Selenium		                <.002	2012	38.  1,1 - Dichloroethylene		<0.5	2013

9.    Beryllium		                <.001	2012	39.  cis-1,2-Dichloroethylene		<0.5	2013

10.  Alachlor		                < 0.5	2011	40.  trans-1,2-Dichloroethylene		<0.5	2013

11.  Di(2-ethylhexyl) adipate	                < 1.5	2011	41.  Thallium			<0.001       2012

42.  1,2-Dichloropropane		<0.5           2013

13.  Chromium		                <.01	2012	43.  Ethylbenzene			<0.5           2013

14.  Endrin			                < 0.5	2011	44.  Styrene			<0.5           2013

15.  Cyanide (have waiver)		 0	1995	45.  1,2,4 –Trichlorobenzene		<0.5           2013

16.  Ethylene dibromide (EDB)	                <.01	2011	46.  1,1,1 - Trichloroethane		<0.5	2013

17.  Hexachlorobenzene (HCB)	                < 0.5	2011	47.  1,1,2 –Trichloroethane		<0.5           2013

18.  Hexachlorocyclo- pentadiene	                < 0.5	2011	48.  Trichloroethylene			<0.5           2013

19.  Oxamyl [Vydate]		                <   1	2011	49.  Toluene			<0.5           2013

20.  Mercury (inorganic)	                < .0005	2012	50.  Xylenes			<0.5           2013

21.  2,4-D			                 <0.1	2011	51.  Atrazine			<0.5	2011

22.  2,4,5-TP(Silvex)		                 <.1	2011	52.  Benzo(a)pyrene(PAH)		<0.1	2011

23.  Carbofuran		                 <  1	2011	53.  Methoxychlor			<0.5	2011

24.  Chlordane		                 <  1	2011	54.  PCBs (Polychlorinaded biphenyls)	  0	1995	  						55.  Picloram			<0.15	2011

26.  Dinoseb		                 <0.1	2011	56.  Simazine			<0.5	2011

27.  Diquat				 0	1995	57.  Benzene			<0.5	2013

28.  Endothall			 0	1995	58.  Tetrachloroethylene		<0.5	2013

29.  Heptachlor		                 <0.2	2011	59.  Vinyl Chloride			<0.5	2013

30.  Heptachlor epoxide	                 <0.1	2011

Sharptown does test for unregulated contaminants not required in this report.  The results of the contaminants not listed above were all non-detected.  A complete list is available at the Town Hall for viewing.

Detected Contaminants NOT in Violation of the MCL

In addition to these un-detected substances that were subject to testing, the Town did find some regulated substances present in the water system at levels below the maximum allowable level (MCL) which is determined safe by the EPA. These substances are shown below, along with the MCL and MCLG for each one detected.

Substances	Year	Level          	Unit 	            MCL              MCLG	     Likely Source of

Tested	Detected         	of 			     	     Contamination

###### Measure-

ment

1. Copper		2011	    0.193		ppm		1.3            AL=1.3	Corrosion of household

plumbing systems; erosion of natural deposits; leaching from wood preservatives

2. Lead		2011	  0.003		ppb		AL=15         0	Corrosion of household

plumbing systems, erosion of natural deposits

3. Nitrate 		2013	 8.89		ppm		10	10	Runoff from fertilizer use;

(as Nitrogen)				leaching from septic tanks,				sewage; erosion of natural 				deposits

4. Barium		2012	 .11		ppm		2	2	Discharge of drilling waste,

discharge from metal refineries,

erosion from natural deposits

5. Fluoride		2012	0.29		ppm		4	4	Erosion from natural deposits,

water additives which promotes

strong teeth, discharge from

fertilizer and aluminum factories

6.  Arsenic		2012	< .002		ppb		10	0	EPA is reviewing the drinking

water standard for arsenic

because of special concerns that it may not be stringent enough. Arsenic is a naturally-occurring mineral known to cause cancer in humans at high concentrations.

7. Di(2-ethylhexyl)phthalate    2011        <1                      ppb	                   6               0                Discharge from rubber and

chemical factories

8. Nitrite		2010	 <  .01		ppm		 1	1	Runoff from fertilizer use;

leaching from septic tanks;

erosion of natural deposits

9. Dalapon 	2011	<.1		ppb		200	200	Runoff herbicide used on

rights of way

It is important to understand that the detection of these substances in the drinking water does not constitute a known threat to public health because they were found only at levels less than the MCL and below the level that EPA currently feels may constitute a health threat. MCL’s are set at very stringent levels, and the Town’s water has proved to be below those levels for the constituents listed above.

The Town found Nitrates and Lead to be present in the water at a level that is in compliance with the MCL, and does not constitute a known threat to public health. The results of that test and the explanation are outlined below.

Detected Contaminant NOT in Violation of the MCL

Contaminant 		Level         	Unit of		MCL	MCLG	 	Likely Source of

Detected          	Measurement 	                   		Contamination

Nitrate (as Nitrogen)		8.90		ppm		10	10	Runoff from fertilizer use;

leaching from septic tanks, of							sewage; erosion of natural							deposits

Nitrates were found at a level of 8.90 parts per million (ppm) in one (1) of the annual tests in our distribution system. This level does not constitute a violation of the Maximum Contaminant Level (MCL) of 10 ppm. We have not found any nitrate levels that exceed the MCL in the past year, but because the level detected at that one site was more than half the allowable MCL, we are required to outline the potential health effects of nitrates in drinking water.

In August of 2008 we had a Nitrate Result of greater than 10 ppm. This was a result of the sample being taken from the wrong sample point. We had the nitrates retested from the proper point immediately and the results were 5.78 ppm. At no time was there any danger to the public or water system.

Nitrate in drinking water at levels above 10 ppm is a health risk for infants less than six months of age. High nitrate levels in drinking water can cause blue baby syndrome. Nitrate level may rise quickly for short periods of time because of rainfall or agricultural activity. If you are caring for an infant you should ask advice from your health care provider. As a precaution we always notify physicians and health care providers in this area if there is ever a higher than normal level of nitrates in the water supply, even when that level does not constitute a violation of the allowable standards.

Lead			  0.003		ppb		AL=15	0	Corrosion of household

Plumbing systems, erosion of

natural deposits

Lead was found at a level of 0.002 parts per billion (ppb) in one (1) of the Triennial tests in our distribution system.  This level does not constitute a violation of the Maximum Contaminant Level (MCL) of  AL=15.  We have not found any lead that exceeds the MCL in the past three years, but because the level detected at the one site was more than half the allowable MCL, we are required to outline the potential health effects of lead in drinking water.

Lead in drinking water at level above AL=15 is a health risk for infants and children who drink water containing lead in excess of the action level could experience delays in their physical or mental development.  Children could show slight deficits in attention span and learning abilities.  Adults who drink this water over many years could develop kidney problems or high blood pressure.  Infants and young children are typically more vulnerable to lead in drinking water than the general population.  It is possible that lead levels at your home may be higher than at other homes in the community as a result of materials used in your home’s pluming.  If you are concerned about elevated lead levels in your home’s water, you may wish to have you water tested and flush your tap for 30 seconds to 2 minutes before using tap water.  Additional information is available from the Safe Drinking Water Hotline (1-800-426-4791).

Detected Contaminant NOT in Violation of the MCL

Contaminant 		Level         	Unit of		 MCL	MCLG	Likely Source of

Detected          	Measurement 	            		Contamination

Radon 222		          50		pCi/L		  N/A	      	 Erosion of natural deposits.

Gross Alpha	                            < 2                  pCi/l                             15             0          Erosion of natural deposits

We constantly monitor the water supply for various constituents.  Test results in 1999 detected radon in the finished water supply in 1 out of 1 sample tested.  There is no federal regulation from radon levels in drinking water.  Exposure to air transmitted radon over a long period of time may cause adverse health effects.

Arsenic			       < .002		ppb		10	      0	   Naturally-occurring mineral

While your drinking water meets EPA’s standard for arsenic, it does contain low levels of arsenic.	  EPA’s standard balances the current understanding of arsenic’s possible health effects against the costs of removing arsenic from drinking water.  EPA continues to research the health effects of low levels of arsenic which is a mineral known to cause cancer in humans at high concentrations and is linked to other health effects such as skin damage and circulatory problems.

For nitrates and the other constituents that were detected at levels lower than the allowable MCL, it is important to understand that the EPA has determined that drinking water IS safe at these allowable levels. MCL’s are set at very stringent levels. To experience the possible health effects described for many of the regulated contaminants, a person would have to drink 2 liters of water every day containing a constituent at the MCL level for a lifetime to have a one-in-a-million chance of having the described health effect.

Usted puede obtener esta informacion en espanol por llamar por telefono la casa del ayuntamiento de Sharptown a 410-883-3767.

Detected Contaminants IN Violation of the MCL

The Town did find levels of TTHM ( Total Trihalomethanes ) present in the water at levels, which constitute a violation of the MCL for those constituents.

TTHM			April 16, 2013		115	ppb		80	By-product of

[Total Trihalomethanes]	July 31, 2013		62	ppb		80	drinking water

September 2013 – Lab Failed To Do Test	ppb		80	chlorination

November 14, 2013	68	ppb		80

TTHM was found at a level higher then the 80 parts per billion (ppb) in annual tests in our distribution system.  These levels did constitute a violation of the Maximum Contaminant Level (MCL) of 80 ppb.  We have found TTHM that exceed the MCL in the past year, because the level detected at the one site was more than the allowable MCL, we are required to outline the potential health effects of TTHM in drinking water.

Some people who drink water containing Trihalomethanes [TTHM] in excess of the MCL over many years experience problems with their liver, kidneys, or central nervous systems, and may have increased risk of getting cancer.

The Town is in the process of conducting more water tests to determine what may be causing the elevated levels of TTHM’s. The Water Department has been in close contact with the Maryland Department of the Environments Water Supply Program for help in determining the possible cause and reviewing possible corrective actions that may correct this situation.

Trihalomethanes [TTHM] in drinking water are created when the Chlorine, used to disinfect the water, reacts with compounds that are found, naturally, in the water pumped from our wells from underground aquifers.

Step number one is to identify the compounds that are creating the TTHM’s. Step number two is to identify which one of the wells the compounds are coming from and then finally step number three would be the corrective action to take.

All sources of drinking water are subject to potential contamination by substances that are naturally occurring or man made. These substances can be microbes, inorganic or organic chemicals and radioactive substances. All drinking water, including bottled water, may reasonably be expected to contain at least small amounts of some contaminants.  The presence of contaminants does not necessarily indicate that the water poses a health risk. More information about contaminants and potential health effects can be obtained by calling the Environmental Protection Agency’s Safe Drinking Water Hotline at 1-800-426-4791.

The presence of some contaminants in drinking water is unavoidable, but we make every effort to keep our water at or below the levels specified by law as being safe for consumption. Our Water Department staff consists of one Maryland State Certified Superintendent and one (Maryland State Temporary Operator) who has a combined experience of almost 20 years between them. Together they have attended many hours of Continuing Education training in the past year in an effort to keep up-to-date with the latest in water treatment techniques to provide you with the best quality water possible. The provision of quality water is an on-going effort for the Town of Sharptown and its staff, and one we are continuously trying to improve upon.

In our continuing efforts to maintain a safe and dependable water supply, the town has authorized a project to install an aeration system inside the water tower. This system will reduce the TTHM level below the Maximum Contaminant Level (MCL) of 80ppb. The costs of these improvements may be reflected in the rate structure. Rate adjustments may be necessary in order to address these improvements. We must set our water rates so that the system pays for itself without subsidy from property tax revenues. In this way, the cost of the water service can be borne by those who actually use water rather than just by the property owners.  At this time there are no anticipated rate increases.

Thank you for allowing us to continue providing your family with clean, quality water this year. In order to maintain a safe and dependable water supply we sometimes need to make improvements that will benefit all of our customers. These improvements are sometimes reflected as rate structure adjustments. Thank you for understanding.

Some people may be more vulnerable to contaminants in drinking water than the general population. Immuno-compromised persons such as persons with cancer undergoing chemotherapy, persons who have undergone organ transplants, people with HIV/AIDS or other immune system disorders, some elderly, and infants can be particularly at risk from infections. These people should seek advice about drinking water from their health care providers. EPA/CDC guidelines on appropriate means to lessen the risk of infection by cryptosporidium and other microbiological contaminants are available from the Safe Drinking Water Hotline (800-426-4791).

We at the Town of Sharptown work continuously to provide top quality water to every tap.

We ask that all our customers help us protect our water sources, which are the heart of our community, our way of life and our children’s future. Please call our office if you have questions.

Sharptown Town Hall – 401 Main Street

Phone – 410-883-3767

FAX – 410-883-3772

Sharptown Water Office – 305 State Street

Phone – 410-883-3805